## EmissionsLimits
Occupancy group | Emissions Intensity Limit (tCO2e/sf) | multiplied by | Corresponding Gross Floor Area (GFA) in sf | Period
1 | A | 0.01074 | X | 2024
2 | B (other than item 6) | 0.00846 | X | 2024
3 | E and I-4 | 0.00758 | X | 2024
4 | I-1 | 0.01138 | X | 2024
5 | F | 0.00574 | X | 2024
6 | B civic administrative facility for emergency response services, B non-production laboratory, Group B ambulatory health care facility, H, I-2 and I-3 | 0.02381 | X | 2024
7 | M | 0.01181 | X | 2024
8 | R-1 | 0.00987 | X | 2024
9 | R-2 | 0.00675 | X | 2024
10 | S and U | 0.00426 | X | 2024
1 | A | 0.0042 | X | 2030
2 | B (other than item 6) | 0.00453 | X | 2030
3 | E and I-4 | 0.00344 | X | 2030
4 | I-1 | 0.00598 | X | 2030
5 | F | 0.00167 | X | 2030
6 | B civic administrative facility for emergency response services, B non-production laboratory, Group B ambulatory health care facility, H, I-2 and I-3 | 0.0133 | X | 2030
7 | M | 0.00403 | X | 2030
8 | R-1 | 0.00526 | X | 2030
9 | R-2 | 0.00407 | X | 2030
10 | S and U | 0.0011 | X | 2030

## CarbonFactors
Energy | Factor | Units | Period
Electric | 0.00028896 | tCO2e/kWh | 2024
N.Gas | 5.311e-05 | tCO2e/kbtu | 2024
Oil2 | 7.421e-05 | tCO2e/kbtu | 2024
Oil4 | 7.529e-05 | tCO2e/kbtu | 2024
Steam | 4.493e-05 | tCO2e/kbtu | 2024